## Tabelle1
Input name | Value | Units | Description | Reference
net_floor_area | 237.6 | m² | Net floor area of the building. | User input
u_windows | 0.8 | W/(m²·K) | U-value (thermal transmittance) of the windows. | User input
u_walls | 0.15 | W/(m²·K) | U-value of the exterior walls. | User input
u_roof | 0.15 | W/(m²·K) | U-value of the roof or ceiling against unheated spaces. | User input
u_base | 0.22 | W/(m²·K) | U-value of the base (floor against ground or basement ceiling against unheated spaces). | User input
temp_adj_base | 1 | - | Temperature adjustment factor for the base | According to DIN EN 18599-2: 1 for transmission towards outdoor or ground 0.5 for transmission towards non-heated spaces
temp_adj_walls_ug | 1 | - | Temperature adjustment factor for walls below ground. | According to DIN EN 18599-2: 1 for transmission towards outdoor or ground 0.5 for transmission towards non-heated spaces
temp_adj_roof | 1 | - | Temperature adjustment factor for the roof or top ceiling against unheated space. | According to DIN EN 18599-2: 1 for transmission towards outdoor or ground 0.5 for transmission towards non-heated spaces
wall_area_og | 232.8 | m² | Wall area above ground. | User input
wall_area_ug | 56.2 | m² | Wall area below ground. | User input
total_window_area | 35.44 | m² | Total area of all windows. | User input
roof_area | 39.9 | m² | Total area of the roof or the top ceiling against unheated space. | User input
base_area | 39.9 | m² | Total area of the base. | User input
t_set_heating | 21 | °C | Set indoor temperature for heating. | Standard value from DIN EN 18599-10 for non-residential buildings. For residential buildings, an average temperature of 21°C is assumed, as heated space can range from 20°C for living spaces to 24°C for bathrooms according to DIN EN 12831.
thermal_bridges_supplement | 0.02 | W/(m²·K) | Thermal bridges surcharge. | User input when value is known, or standard input otherwise. Loga et al. classify thermal bridges surcharges in 4 levels: - minimal (0 W/m²K) for buildings with thermally optimized junctions - low (0.05 W/m²K) for buildings with low thermal bridging effects - medium (0.1 W/m²K) when parts of the envelope asre penetrated by elements with higher thermal conductivity - high (0.15 W/m²K) when parts of the envelope asre penetrated by elements with very high thermal conductivity For more details, see Loga et al. 2019 "TABULA Calculation Method – Energy Use for Heating and Domestic Hot Water"
gross_building_vol | 815.9 | m³ | Gross volume of the building. | User input
net_building_vol | 652.72 | m³ | Net volume of the building. | User input
reference_vol_name | "net" | - | Volume used as reference for ventilation (net or gross). | User input
t_norm_ext_heating | -12.1 | °C | Normalized external temperature for heating load. | The standard temperatures on the design day can be found in DIN TS 12831-1, and also here https://www.waermepumpe.de/werkzeuge/klimakarte/
heat_rec_vent | 0.8 | - | Heat recovery rate of the ventilation system. | User input when value is known, typically between 0.6 and 0.8
ach_min | 0.5 | 1/h | Minimum air change rate. | Standard DIN EN 18599 for residential buildings, and empirical values for non-residential buildings from: https://github.com/IWUGERMANY/Non-domestic-multi-zone-average-usage-profiles-for-Germany
ach_infl | 0.04 | 1/h | Air change rate due to infiltration. | Simple calculation of the infiltration based on DIN EN 18599-2, with a wind protection coefficient of 0.07. The following values can be assumed, depending on the state of the thermal envelope: Passive house requirement fulfilled: 0.04 h-1 New building with airtightness test and mechanical ventilation system: 0.07 h-1 New building with airtightness test without mechanical ventilation system: 0.14 New building without airtightness test: 0.28 Existing building without airtightness test: 0.42 Existing building with obvious leaks: 0.7
ach_vent | 0.4 | 1/h | Air change rate due to mechanical ventilation. | User input. Typical assumption: 80% of ach_min
share_heated | 1 | - | Share of the building that is heated. | User input. Default value: 1
share_cooled | 1 | - | Share of the building that is cooled. | User input. Default value: 1
share_mech_ventilated | 1 | - | Share of the building with mechanical ventilation. | User input. Default value: 1
t_norm_ext_cooling_july | 25 | °C | Standard outdoor temperature on design day in July for cooling load. | Based on standard VDI 2078, depending on the cooling zone
t_norm_ext_cooling_sept | 20.3 | °C | Standard outdoor temperature on design day in September for cooling load. | Based on standard VDI 2078, depending on the cooling zone
gtot | 0.23 | - | Total window energy transmittance (glazing + shading). | Based on DIN EN 18599-2, table 8
share_glass_frame | 1 | - | Share of window area taken up by glass, without frame. | User input, typically 0.7
t_set_cooling | 25 | °C | Indoor setpoint temperature for cooling. | Typical values from DIN EN 18599-10 or empirical values from https://github.com/IWUGERMANY/Non-domestic-multi-zone-average-usage-profiles-for-Germany
t_set_cooling_max | 26 | °C | Maximum permissible indoor temp. during cooling. | Typical values from DIN EN 18599-10 or empirical values from https://github.com/IWUGERMANY/Non-domestic-multi-zone-average-usage-profiles-for-Germany
phi_i_cooling_spec | 1.875 | W/m² | Specific internal heat gains during cooling. | Typical values from DIN EN 18599-10 or empirical values from https://github.com/IWUGERMANY/Non-domestic-multi-zone-average-usage-profiles-for-Germany